## Sheet1
DOMESTIC FILL STATION SCHEDULE
TAG | TYPE | DESCRIPTION | SIZE | MODEL | NOTES
DFV-1 | FILL VALVE | SOLENOID ACTUATED FILL VALVE | 2" | CLA-VAL 136-01AC-KC-SS | 1,2,8,9
DFV-2 | FILL VALVE | SOLENOID ACTUATED FILL VALVE | 2" | CLA-VAL 136-01AC-KC-SS | 1,2,8,9
DBV-1 | FLOOD PROTECTION BLOCK VALVE | MOTORIZED BUTTERFLY VALVE | 3" | COUGAR SYSTEMS MOBFV 300 | 1,3,8,9
DS-1 | STRAINER | WYE STRAINER WITH BUTTERFLY VALVE | 3" | NEXUS STRAINEX SXFV | 1,4,8,9
DLCP-1 | CONTROL PANEL | PLC BASED LEVEL CONTROL PANEL |  | COUGAR SYSTEMS ET11F2B1T1 | 1,5,6,7,8,9
NOTES: 1. REFER TO DOMESTIC WATER STORAGE TANK FILL STATION DETAIL 2. VALVE TRIM TO INCLUDE CLOSING SPEED, STRAINER, EPOXY COATED AND STAINLESS STEEL TRIM 3. NSF 61 VALVE WITH A 120V ACUATOR 4. STRAINER COMPLETE WITH BUTTERFLY VALVE, STRAINER & BLOW-DOWN VALVE 5. LEVEL CONTROL DONE BY PRESSURE TRANSDUCER WITH BACK UP HIGH LEVEL PROBE 6. TANK LEVEL & SET POINTS DISPLAYED IN INCHES 7. MONITOR CITY PRESSURE WITH PRESSURE TRANSMITTER 8. START-UP DONE BY SYSTEM SUPPLIER. 9. FIELD WIRING FROM CONTROL PANEL TO VALVES AND LEVEL SENSOR ASSEMBLY BY SYSTEM SUPPLIER