## Sheet1
COMBINATION FIRE/DOMESTIC WATER STORAGE TANK SCHEDULE
TAG | USEABLE CAPACITY (GALLONS) | DIMENSIONS (L x W x H) | TYPE | MODEL | NOTES
ST-1 | 3,500 FIRE / 1,000 DOMESTIC | 14'-9" x 8'-2" x 8'-2" | FIELD BUILT BOLTED FIBERGLASS | FTC-3500/1000 | ALL
NOTES: 1. FOR TANK CONNECTIONS REFER TO COMBINATION FIRE/DOMESTIC WATER STORAGE TANK DETAIL 2. TANK TO BE INSTALLED BY SUPPLIER 3. TANK TO BE INSTALLED ON ENGINEERED STEEL BASE WITH MODULAR STEEL PEDESTAL FOOTING 4. TANK TO HAVE DOUBLE WALL PARTITION WITH A 4" AIR GAP TO SEPARATE FIRE & DOMESTIC COMPARTMENT 5. SCHEDULED HEIGHT INCLUDES MODULAR STEEL PEDESTALS 6. TANK MUST BE COMPLIANT WITH AWWA D12-121 AND NSF 61 WITHOUT A LINER 7. SHEET MOLDING COMPOUND TO BE HOT PRESSED AT 300° F AND 3000 PSI 8. TANK SEALANT TO BE A SOLID SYNTHETIC RUBBER SEALANT RIBBED IN NO LESS THAN 4 LOCATIONS 9. ALL HARDWARE TO BE 316 STAINLESS STEEL